## HU English Version
H Series inverter/UPS 300-1200W series
Technical specifications
Model No：HU |  | 30112 | 50112 | 50124 | 10212 | 10224 | 12224
Rated power ( W ) |  | 300W | 500W |  | 1000W |  | 1200W
Peak power ( ms ) |  | 600W | 1000W |  | 2000W |  | 2400W
Nominal battery voltage ( Vdc ) |  | 12V | 12V | 24V | 12V/24V/48V
Installation method |  | Wall mounting
Machine Size (L*W*H mm) |  | 350*305*130
Package Size(L*W*H mm) |  | 440*380*230
Net Weight(kg) |  | 22Kg | 7.5Kg |  | 9.5Kg |  | 10.6Kg
Gross Weigt(kg)（Carton package） |  | 23Kg | 8.5Kg |  | 10.4kg |  | 11.5Kg
General parameters
Input | Battery input voltage range | 10.5V-15V(Single battery voltage）
| Input phase system | L+N+PE
| AC input voltage range | 75-135Vac/145-265Vac
| AC input frequency range | 40-65HZ
| Mains low voltage to battery | 75Vac/145Vac±5%
| Mains power low voltage restored | 85Vac/155Vac±5%
| Mains high voltage to battery | 135Vac/265Vac±5%
| Mains high voltage restored | 125Vac/255Vac±5%
Output | Output phase system | L+N+PE
| The output voltage | 110Vac/120Vac/220Vac/230Vac/240Vac±5(Inverter mode）
| AC frequency | 50/60Hz±1% (Inverter mode）Mains automatic tracking and synchronization
| Output waveform | pure sine wave
| Inverter no-load loss | ≦20W
| Inverter efficiency | ≥90%（88% resistive load）
| Mains efficiency | ≥99%（No charging status）
| Harmonic distortion | THD≦3%(resistive load）
Operating mode | Mains power priority | National grid power supply Priority, and automatically switch to inverter (battery) state when the power grid fails.
| Energy saving mode | When no load is detected in the inverter state, it automatically switches to sleep state (to save reserve power) and is suitable for special scenarios
| Solar energy first | Photovoltaic power generation priority. When photovoltaic power generation is insufficient, it will automatically transfer to the mains power supply. When photovoltaic power is restored, it will automatically transfer to photovoltaic priority power supply
Battery input |  | Lead-acid, gel, AGM battery custom settings
Lithium battery (factory set)
Protective function |  | Overvoltage, undervoltage, overload, short circuit, overtemperature, overcurrent, surge, etc.
Panel display |  | LCD+LED
Heat dissipation method |  | Forced air cooling
conversion time |  | ≦4ms(Typical load）
Communication (optional) |  | RS232/RS485/Mob APP（WIFI/GPRS)
Environment | Operating temperature | -10℃~40℃
| Storage temperature | -15℃~60℃
| Altitude | 2000m（Derating is required if the amount exceeds the limit.）
| Noise | ≤65dB
| Relative humidity | 0%~95% ,No condensation
Advantages and features：
◆ Power frequency energy-saving transformer, full-bridge pure sine wave output, low loss and high efficiency;
◇ Three Modes Free switching , mains priority/power saving mode/photovoltaic priority settable, flexible application
◆ It has two working modes: mains bypass and inverter output, and has UPS uninterruptible power supply;
◇ Can be equipped with an external solar controller to form a solar power generation system;
◆ LCD+LED dual display, you can know the operating status of the system at any time, and the data is clear at a glance;
◇ Efficient and intelligent, remote control, unattended function;
◆ Supports multiple communication interface options, remote monitoring (RS232/mobile APP (WIFI/GPRS)
Product parameters